## Matrix
[6 empty] | Construction | Child under 2.5 | New/Existing | Classroom 2.5 | LED | LED- | LED+ | Occ Classification | Occ Load | Occ Class | kids>5 | kids+exit | #of kids | Occupancy | Below LED | Footage | Constr | Kids>100 | rc&l
Child Daycare Center Classification Matrix | [12 empty] | Group E | F/A | F/A | Occupant | F/A | Occupant | Sprinkler | Sprinkler | Sprinkler | Sprinkler | Sprinkler
| Orange boxes must be answered "Yes" or "No" |  | Occupancy Classification, Fire System Requirements |  |  | Yes | Yes | New | Yes | Yes | Yes | Yes | Group I-4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
| Yellow boxes must have a number value added |  | and Classroom Exit Requirements |  |  | No | No | Existing | No | No | No | No |  |  |  |  | Occupant
| Green boxes are the answers based on what you input |  | Occupancy Classification | Group E | [12 empty] | 1
Sprinkler
More than 5 children under 2.5 years of age? |  |  | Fire Alarm System Required? | No | [12 empty] | 1
Number of children 2.5 years of age or less |  |  | Fire Sprinkler System Required? | No
Number of children over 2.5 years of age
Total number of children |  | 0 | When are 2 exits required for classrooms
|  |  | containing children under 2.5 years of age? | 11 | Occupants
Does every classroom with children under 2.5 years of age
have an exterior exit door at level of exit discharge? |  |  | When are 2 exits required for classrooms
|  |  | containing children over 2.5 years of age? | 50 | Occupants
Are there any classrooms other than the level of exit discharge?
Total square footage of the fire area?
Is the building Type V-B construction over 9,500 square feet?
*NOTE* All yellow/orange boxes must be completed for an accurate response

## Group E Occupancy Checklist
Group E Child Daycare Center Inspection Checklist
Y=Meets Requirements; N=Does Not Meet Requirements
Y | N |  | Y | N
|  | Group E Child Daycare Center |  |  | Fire Extinguishers
|  | (MSFC Group I-4, Day Care Facility definition) |  |  | 2-A:10B:C provided within 75 feet of travel distance
|  | All children over 2.5 years of age |  |  | (MSFC 906.3)
|  | No more than 5 children under 2.5 years of age |  |  | Class K provided in kitchen when cooking with
|  | More than 5 children under 2.5 years of age IF |  |  | animal or vegetable oils and fats (MSFC 906.4)
|  | every classroom has direct exterior exit on LED |  |  | Inspected annually (MSFC 901.6.1)
|  | EXTERIOR: |  |  | Classroom exits
|  | Address visible (MSFC 505.1) |  |  | 2 required in classrooms with children over 2.5 years
|  | Fire hydrants/water supply accessible (MSFC 507) |  |  | of age when occupant load exceeds 49
|  | Combustible accumulations/storage acceptable |  |  | (MSFC 1006.2.1, 1104.25)
|  | (MSFC 304.1, 315.4) |  |  | Existing (pre 2003) classrooms require 2 exits when
|  | Gas meter/piping protected against impact |  |  | over 1,000ft2
|  | (MSFC 312, 603.9) |  |  | 2 required in classrooms with children under 2.5
years of age when occupant load exceeds 10
|  | Fire Alarm System |  |  | (MSFC 1006.2.1, 1104.25)
Required when over 49 occupant load
|  | (MSFC 907.2.3, 1103.7.2) |  |  | Building/Floor Exits
|  | Existing-Not required if building is less than 1,000ft2 |  |  | 2 required when building or floor occupant load
|  | and no closer than 20ft from another building |  |  | exceeds 49 (MSFC 1006.2.1, 1104.25)
|  | (MSFC 1103.7.2.1) |  |  | 2 always required when above the level of exit
|  | Fire detection in laundry, boiler, furnace, mechanical |  |  | discharge (MSFC 1006.3.3, 1104.25)
and electrical rooms, shops, kitchens, custodial
|  | closets, trash and storage rooms and similar areas |  |  | Travel Distance (MSFC 1017.2, 1104.17.4)
|  | (MSFC 907.2.3.1, 1103.7.2.2) |  |  | No fire sprinkler system = 200ft
|  | Manual pull stations permitted to be in main office, |  |  | Complete fire sprinkler system = 250ft
custodial office, kitchen and boiler room IF corridors
|  | protected with automatic fire sprinkler system OR |  |  | Corridors
|  | corridor smoke detection system |  |  | NEW-Minimum 44" wide (MSFC 1020.2)
|  | (MSFC 907.2.3.1, 1103.7.2.2.1) |  |  | New-Minimum 72" wide when occupant load is 100
|  | Fire alarm shall signal a General Evacuation only |  |  | or more (MSFC 1020.2)
|  | (MSFC 907.2.3.3, 1103.7.2.4) |  |  | Existing-Minimum 36" wide but not less than
|  | Inspected annually (MSFC 901.6.1) |  |  | calculated per Section 1005.3 (MSFC 1104.17.3.1)
1-hour fire rated when more than 30 occupants
|  | Fire Sprinkler System - NEW Only |  |  | unless complete fire sprinkler system OR every
|  | Throughout all Group E fire areas greater than |  |  | classroom has direct exterior exit on grade
|  | 12,000ft2 (MSFC 903.2.3) |  |  | (MSFC 1020.1)
|  | Whenever the Group E fire area is located on a floor |  |  | Existing non-complying corridors permitted with a
|  | other than a level of exit discharge (MSFC 903.2.3) |  |  | monitored fire alarm system with corridor smoke
|  | Occupant load of 300 or more (MSFC 903.2.3) |  |  | detection (MSFC 1104.17.1.3)
Inspected annually (MSFC 901.6.1)
Y=Meets Requirements; N=Does Not Meet Requirements
Y | N |  | Y | N
|  | Interior Finish |  |  | Electrical
|  | Exposed foam plastics (including vinyl covered) |  |  | No electrical hazards (MSFC 604.1)
|  | meets NFPA 286 (MSFC 803.11) |  |  | Appliances/fixtures in good condition (MSFC 604.7)
|  | Decorations and artwork limited to 20% of |  |  | Overcurrent protection present (MSFC 604.4.1)
|  | wall space, 50% when protected by complete |  |  | Multi-plug adapters per NFPA 70 (MSFC 604.4)
|  | fire sprinkler system (MSFC 807.5.2.2, 807.5.2.3) |  |  | Extension cords not substituted for fixed wiring
|  | No clothing or personal effects stored in corridor |  |  | (MSFC 604.5)
|  | unless protected by complete fire sprinkler system OR |  |  | Power strips properly used (MSFC 604.4.3)
stored in metal lockers (MSFC 807.5.2.1)
|  | Interior finishes meet minimum requirements of |  |  | Emergency Planning and Preparedness
|  | MSFC Table 803.3 |  |  | Fire evacuation and safety plans provided
(MSFC 403.5)
|  | Storage |  |  | Evacuation plans conducted monthly (MSFC 405.2)
|  | Storage neat and orderly (MSFC 315.3) |  |  | Employees trained annually (MSFC 406.2)
LP tanks not stored indoors (MSFC Chapter 61)
|  | Fueled equipment (lawn mower, snowblower, etc) |  |  | Carbon Monoxide Detection
|  | stored outside or in room built for such storage |  | (SFMD Group E and I-4 Occupancies Information Sheet)
|  | (MSFC 313.1) |  |  | Required in NEW occupancies only
Installed as required (MSFC 915)
Utility/Mechanical/HVAC
Shut off valves present on gas appliances (MSFC 603.1)
Approved piping, connections and appliances used
(MSFC 603.1.2)
Combustion air supply/venting present (MSFC 603.1)
Adequate clearance between combustibles and
appliances (MSFC 305.1, 603.5.3)
Version 2.0 Effective March 31, 2020
Revised March 23, 2021
This checklist is intended as a guide to assist fire inspection personnel in identifying general fire and life safety hazards.
Other code requirements may apply. Please refer to the other SFMD checklists for information not provided herein.
MSFC = Minnesota State Fire Code SFMD = State Fire Marshal Division

## Group I-4 Occupancy Checklist
Group I-4 Child Daycare Center Inspection Checklist
Y=Meets Requirements; N=Does Not Meet Requirements
Y | N |  | Y | N
|  | Group I-4 Child Daycare Center |  |  | Fire Extinguishers
|  | (MSFC Group I-4, Day Care Facility definition) |  |  | 2-A:10B:C provided within 75 feet of travel distance
|  | More than 5 children under 2.5 years of age IF |  |  | (MSFC 906.3)
|  | such classrooms do not have direct exterior |  |  | Class K provided in kitchen when cooking with
|  | exit on level of exit discharge (LED) |  |  | animal or vegetable oils and fats (MSFC 906.4)
|  | More than 100 children under 2.5 years of age |  |  | Inspected annually (MSFC 901.6.1)
|  | EXTERIOR: |  |  | Classroom exits
|  | Address visible (MSFC 505.1) |  |  | 2 required in classrooms when occupant load
|  | Fire hydrants/water supply accessible (MSFC 507) |  |  | exceeds 10 (MSFC 1006.2.1, 1104.25)
Combustible accumulations/storage acceptable
|  | (MSFC 304.1, 315.4) |  |  | Building/Floor Exits
|  | Gas meter/piping protected against impact |  |  | 2 required when building or floor occupant load
|  | (MSFC 312, 603.9) |  |  | exceeds 10 (MSFC 1006.2.1, 1104.25)
2 always required when above the level of exit
|  | Fire Alarm System |  |  | discharge (MSFC 1006.3.3, 1104.25)
Required (MSFC 907.2.6.4, 1103.7.3)
|  | Fire detection in laundry, boiler, furnace, mechanical |  |  | Travel Distance (MSFC 1017.2, 1104.17.4)
|  | and electrical rooms, shops, kitchens, custodial |  |  | No fire sprinkler system = 200ft
|  | closets, trash and storage rooms and similar areas |  |  | Complete fire sprinkler system = 250ft
(MSFC 907.2.6.4.1, 1103.7.3)
|  | Smoke detection provided in corridors and spaces |  |  | Corridors
|  | open to the corridors (MSFC 907.2.6.4.1, 1103.7.3) |  |  | NEW-Minimum 44" wide (MSFC 1020.2)
|  | Fire alarm shall signal a General Evacuation AND |  |  | Existing-Minimum 36" wide but not less than
|  | shall transmit to a central or remote station |  |  | calculated per Section 1005.3 (MSFC 1104.17.3.1)
|  | service (MSFC 907.2.6.4.2, 1103.7.3) |  |  | 1-hour fire rated when more than 10 occupants
|  | Inspected annually (MSFC 901.6.1) |  |  | unless complete fire sprinkler system installed
(MSFC 1020.1, 1104.17.1)
Fire Sprinkler System - NEW Only
|  | Required (MSFC 903.2.6) |  |  | Interior Finish
|  | Not required if located on the level of exit discharge |  |  | Exposed foam plastics (including vinyl covered)
|  | and every classroom has an exterior exit LED |  |  | meets NFPA 286 (MSFC 803.11)
|  | (MSFC 903.2.6 Exception 2) |  |  | Decorations and artwork limited to 20% of
|  | On floor other than the level of exit discharge, |  |  | wall space, 50% when protected by complete
|  | every floor between the care floor and exit shall |  |  | fire sprinkler system (MSFC 807.5.5.2, 807.5.5.3)
|  | have a complete fire sprinkler system |  |  | No clothing or personal effects stored in corridor
|  | (MSFC 903.2.6 Exception 3) |  |  | unless protected by complete fire sprinkler system OR
|  | Inspected annually (MSFC 901.6.1) |  |  | stored in metal lockers (MSFC 807.5.5.1)
Interior finishes meet minimum requirements of
MSFC Table 803.3
Y=Meets Requirements; N=Does Not Meet Requirements
Y | N |  | Y | N
|  | Storage |  |  | Electrical
|  | Storage neat and orderly (MSFC 315.3) |  |  | No electrical hazards (MSFC 604.1)
|  | LP tanks not stored indoors (MSFC Chapter 61) |  |  | Appliances/fixtures in good condition (MSFC 604.7)
|  | Fueled equipment (lawn mower, snowblower, etc) |  |  | Overcurrent protection present (MSFC 604.4.1)
|  | stored outside or in room built for such storage |  |  | Multi-plug adapters per NFPA 70 (MSFC 604.4)
|  | (MSFC 313.1) |  |  | Extension cords not substituted for fixed wiring
(MSFC 604.5)
|  | Utility/Mechanical/HVAC |  |  | Power strips properly used (MSFC 604.4.3)
Shut off valves present on gas appliances (MSFC 603.1)
|  | Approved piping, connections and appliances used |  |  | Emergency Planning and Preparedness
|  | (MSFC 603.1.2) |  |  | Fire evacuation and safety plans provided
|  | Combustion air supply/venting present (MSFC 603.1) |  |  | (MSFC 403.5)
|  | Adequate clearance between combustibles and |  |  | Evacuation plans conducted monthly (MSFC 405.2)
|  | appliances (MSFC 305.1, 603.5.3) |  |  | Employees trained annually (MSFC 406.2)
Carbon Monoxide Detection
(SFMD Group E and I-4 Occupancies Information Sheet)
Required in NEW occupancies only
Installed as required (MSFC 915)
Version 2.0 Effective March 31, 2020
Revised March 23, 2021
This checklist is intended as a guide to assist fire inspection personnel in identifying general fire and life safety hazards.
Other code requirements may apply. Please refer to the other SFMD checklists for information not provided herein.
MSFC = Minnesota State Fire Code SFMD = State Fire Marshal Division